## Calculations
Induction Unit Replacement - Fan Energy Savings |  |  |  |  | Input Unit System: |  |  | IP
|  |  | Current System |  |  | New System
| Total System Airflow |  | 40000 | CFM |  | 22000 | CFM
| System Static |  | 6 | In. w.c. |  | 1.815 | In. w.c.
| Unit Static |  | 1.8 | In. w.c. |  | 0.6 | In. w.c.
| Fan Efficiency |  | 70% |  |  | 70%
| Fan Power Consumption = |  | 70.259 | hp |  | 11.9643 | hp
Energy Savings
|  | Operation time |  |  | 18 | Hrs/Day
[5 empty] | 365 | Days/year
|  | Electricity Cost |  |  | 0.15 | $/kWh
|  | Capital & Installation Costs |  |  | 800000
|  | 285715.034 | kWh | --- | 42857.2551 | Per Year
|  | Simple Payback: |  |  | 18.6666 | Years
|  | Simple ROI: |  |  | 5.357%

## Notes
IP
Metric | 1. Only Input into yellow cells.
2. System static pressure is the supply fan's external static pressure drop, not including that of the induction unit.
3. New system pressure calculation is based on the assumption that only the induction units are being replaced - the rest of the air distribution system is left unchanged.
4. Units of inputs are not automatically converted when unit system is changed.